- Fire watchers are required whenever welding or cutting is performed in locations where a fire might develop, or any of the following conditions exist:

  - Appreciable combustible material in building construction or contents closer than 50 feet to the point of operation.

  - Appreciable combustibles are more than 50 feet away but are easily ignited by sparks.

  - Wall or floor openings are within a 50-foot radius expose combustible material in adjacent areas including concealed spaces in walls or floors.

  - Combustible materials are next to the opposite side of metal partitions, walls, ceilings, or roofs and are likely to be ignited by conduction or radiation.

- Fire Watchers shall have fire-extinguishing equipment readily available and be trained in its use.

- They shall be familiar with facilities for sounding an alarm in case of a fire.

- They shall watch for fires in all exposed areas, try to extinguish them only when obviously with in the role of the equipment available, or otherwise sounds the alarm.

- A fire watch shall be maintained for at least a half hour after completion of welding or cutting operations to detect and extinguish possible smoldering fires.

- When you are assigned the task of FIREWATCH, you shall read and acknowledge that you understand the following instructions:

  - When you serve as Fire watch, you have NO OTHER ASSIGNMENTS.

  - A welder typically cannot see a fire starting when welding because of his hood.

  - Your job is to be continuously watching the area where hot work might cause a fire to start. YOU MUST WATCH THE WORK AREA; YOU MUST NOT BE LOOKING OFF SOMEWHERE ELSE.

  - You are to continuously remain at the location where the hot work is taking place. If you have to leave, hot work must stop.

  - You are to obtain an extinguisher that has been inspected within last 12 months and position the extinguisher where it can be easily accessible for use if a fire develops. DO NOT PULL THE PIN OR CHARGE UP THE EXTINGUISHER unless it becomes necessary to use the extinguisher.

  - You are performing an important job in preventing fires.

  - Never look directly at the welder’s arc. If welding is taking place on a foggy day or at night, green tinted safety glasses should be worn.

  - You are to stay at the site for 30 minutes after the job is completed. (Unless you are relieved by SUIT Risk Management Office.)

  - Return the firefighting equipment to the proper location upon completion of the hot work.

  - For all PF Campus locations: You shall be given a provided a radio, in case of an uncontrolled fire or the fire is beyond the capacity of the equipment available to you, you shall notify the PF’s SUPD/Dispatch immediately to begin the emergency action plan. In the event you cannot contact the control room, or immediate danger is present, you are authorized to shut down the immediate area and evacuate the facility via the nearest exit and assemble at the Muster Area.

| I certify that I have received firefighting and hand-held extinguisher training within the last year, and I understand and will follow the above instructions. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Print Name (Fire Watch): |  |  | Company: |  |  |
| Signature (Fire Watch): | #### X |  | Date: |  |  |
| I acknowledge the responsibilities of the Fire Watch during the hot work operation. |  |  |  |  |  |
| Print Name (Craftsman): |  | Signature (Craftsman): |  | #### X |  |
| Contact Information: |  |  |  |  |  |